## 42 Temp Test SKU2
Temperature Test: UL 916, Clause 42
Test Purpose:
To determine whether the equipment is capable of normal operation according to intended ratings.
Test Parameters:
Test Parameters | Input Voltage |  |  |  | 120/240 |  |  |  | Output Voltage |  |  |  | 120/240
| Input Current Max |  |  |  | 200 |  |  |  | Output Currents Max |  |  |  | 200
| Input Frequency |  |  |  | 60 |  |  |  | Output Frequency |  |  |  | 60
Ambient Test Temperature | Between 10°C to 40°C
Sample No.
Test | The equipment under test is to be mounted in a manner that simulates its intended use, operated under normal conditions and shall carry its rated current continuously at the test voltage specified in UL 916, Table 40.1; until temperatures are constant. A protective device shall not trip during the test. Permanently-connected equipment is to be tested with 4 feet (1.22 m) of wire attached to each field-wiring terminal. The wire is to be of the smallest size having an ampacity of at least 125 percent of the test current for motor loads, continuous duty loads, and combination loads, and at least 100 percent for other loads. Wire size is to be determined in accordance with Table 310-16 of the National Electrical Code, ANSI/NFPA 70. The size is to be based upon wire that is rated for a temperature of 60°C (140°F) for a rating of 100 amperes or less. Permanently-connected equipment is to be installed so that it is located as close to the wall or corner as the construction will permit. Doors and covers that may be closed during operation of the equipment are to be closed during the test. Other than at coils, temperatures are to be measured by thermocouples consisting of wires not larger than 24 AWG (0.21 mm2). The thermocouple wire is to comply with the requirements for thermocouples as specified in the Tolerances on Initial Values of EMF versus Temperature tables in the Standard Specification and Temperature-Electromotive Force (emf) Tables for Standardized Thermocouples, ANSI/ASTM E230/E230M. A temperature is considered to be constant when three successive readings, taken at intervals of 10 percent of the previously elapsed duration of the test, but not less than 5-minute intervals, indicate no change, and when three successive readings, taken at intervals of 10% of the previously elapsed duration of the test (but not less than 10 min), are constant within 1C. A thermocouple junction and adjacent thermocouple lead wire are to be securely held in good thermal contact with the surface of the material under test. The thermocouple method consists of the determination of temperature by the application of thermocouples to the hottest accessible parts. Temperature data shall be corrected to maximum rated ambient temperature. Attach thermocouples to the points listed below and record the peak temperatures and time attained.
Results:
Input Voltage: |  | 120/240 |  |  |  |  | Output Voltages: |  |  |  |  | 120/240
Input Frequency: |  | 60 |  |  |  |  | Output Frequency: |  |  |  |  | 60
Input Current: |  | 200 |  |  |  |  | Output Currents: |  |  |  |  | 200
|  |  |  | Temperature file: |  |  |  | UL916_Cls.42TempTestData.xlsx | [7 empty] | Allowable
TC Channel & Location | [5 empty] | 0 min | 15 | 30 | 45 | 60 | 75 | Ambient[C] | Temp Rise From Ambient [C] | Max Temp Recorded[C] |  | Max temperature [C] | Rise [C] | data logger file
Gasket | [5 empty] | 25.6 | 27.6 | 32.4 | 35.8 |  |  | 27.4 | 25.1 |  | 25.1 | 100
Supply Lug | [5 empty] | 25.2 | 64.8 | 80.1 | 76.2 |  |  |  | 25.1 |  | 25.1 |  | 50
Backup Lug | [5 empty] | 24.8 | 42.4 | 58.3 | 62.6 |  |  |  | 25.1 |  | 25.1 |  | 50
Subpanel lug | [5 empty] | 24.9 | 59.2 | 77.5 | 78.3 |  |  |  | 25.1 |  | 25.1 |  | 50
MSA busbar | [5 empty] | 25.2 | 68.3 | 90.2 | 92.4 |  |  |  | 25.1 |  | 25.1 |  | 65
Glass door | [5 empty] | 25.5 | 26.9 | 30.7 | 33.9 |  |  |  | 25.1 |  | 25.1 | 95
Upper enclosure ambient | [5 empty] | 25.7 | 35.3 | 47.6 | 49.8 |  |  |  | 25.1 |  | 25.1 |  | NA
Lower enclosure Ambient | [5 empty] | 25 | 30.9 | 38.3 | 41.4 |  |  |  | 25.1 |  | 25.1 |  | NA
Subpanel tray | [5 empty] | 24.9 | 54.1 | 71.6 | 72.9 |  |  |  | 25.1 |  | 25.1 | 125
Ambient under MSA cover | [5 empty] | 25.6 | 49.7 | 71 | 74.8 |  |  |  | 25.1 |  | 25.1 |  | NA
MSA PCB | [5 empty] | 25.5 | 64.7 | 87.4 | 89.5 |  |  |  | 25.1 |  | 25.1 | 130
MCB plastic | [5 empty] | 24.7 | 52.2 | 78.8 | 84.7 |  |  |  | 25.1 |  | 25.1 | 100
Enclosure handle | [5 empty] | 26 | 30.5 | 38.2 | 42.4 |  |  |  | 25.1 |  | 25.1 | 60
Top of enclosure (plastic) | [5 empty] | 26.6 | 31.8 | 36.5 | 49.4 |  |  |  | 25.1 |  | 25.1 | 105
Side of enclosure | [5 empty] | 25.7 | 35.4 | 46.2 | 50.7 |  |  |  | 25.1 |  | 25.1 | 60
subpanel bussing | [5 empty] | 24.7 | 58.2 | 75.4 | 75.1 |  |  |  | 25.1 |  | 25.1 |  | 65
Eaton branch breaker 125A plastic (top) | [5 empty] | 26 | 29.9 | 36.2 | 42.9 |  |  |  | 25.1 |  | 25.1 | 125
Eaton branch breaker 125A plastic (middle) | [5 empty] | 25 | 50.7 | 66.6 | 62.7 |  |  |  | 25.1 |  | 25.1 | 125
Eaton branch breaker 125A bussing (top) | [5 empty] | 24.9 | 59.3 | 77.6 | 72.6 |  |  |  | 25.1 |  | 25.1 |  | 65
Eaton branch breaker 125A bussing (middle) | [5 empty] | 24.8 | 63.6 | 81.3 | 76.8 |  |  |  | 25.1 |  | 25.1 |  | 65
Transformer cover (plastic) | [5 empty] | 25.9 | 42.2 | 58.9 | 65.4 |  |  |  | 25.1 |  | 25.1 | 105
RF window plastic | [5 empty] | 24.9 | 26.2 | 27.7 | 28.8 |  |  |  | 25.1 |  | 25.1 | 85
busbar tray near MCB | [5 empty] | 24.7 | 56.4 | 85.9 | 91.3 |  |  |  | 25.1 |  | 25.1 | 105
busbar tray near field wiring | [5 empty] | 24.6 | 36.6 | 50.2 | 55.3 |  |  |  | 25.1 |  | 25.1 | 105
busbar tray near MSA (under cover) | [5 empty] | 24.6 | 63.4 | 93 | 98.2 |  |  |  | 25.1 |  | 25.1 | 105
Relay ambient | [5 empty] | 25.7 | 33.3 | 51.8 | 50.5 |  |  |  | 25.1 |  | 25.1 | 85
MCB ambient | [5 empty] | 24.7 | 44.7 | 63.1 | 72.2 |  |  |  | 25.1 |  | 25.1 | 40
Lab ambient | [5 empty] | 25.1 | 25.6 | 26.8 | 28.1 |  |  |  | 25.1 |  | 25.1 |  | NA
Capacitor (C44) | [5 empty] | 24.6 | 55.7 | 82.7 | 89.1 |  |  |  | 25.1 |  | 25.1 | 105
TACO PCB | [5 empty] | 25.8 | 49.4 | 59.2 | 59.4 |  |  |  | 25.1 |  | 25.1 | 105
Yellow Connector under MSA | [12 empty] | 25.1 |  | 25.1
Green Connector under MSA | [12 empty] | 25.1 |  | 25.1
Red Connector under MSA | [12 empty] | 25.1 |  | 25.1
Red wire under MSA board | [12 empty] | 25.1 |  | 25.1 | 75
Black wire under MSA board | [12 empty] | 25.1 |  | 25.1 | 75
Yellow wire under MSA board | [12 empty] | 25.1 |  | 25.1 | 75
winding internal side of Transformer | [5 empty] | 26 | 30.3 | 37.2 | 43.4 |  |  |  | 25.1 |  | 25.1 | 200
Windings of Transformer | [5 empty] | 26 | 28.3 | 34.3 | 40.8 |  |  |  | 25.1 |  | 25.1 | 200
busbar L1 from Neutral Balancer to relay | [5 empty] | 25 | 56 | 76.9 | 81.1 |  |  |  | 25.1 |  | 25.1 |  | 65
busbar L2 from Neutral Balancer to relay | [5 empty] | 24.7 | 60.5 | 83.6 | 87.1 |  |  |  | 25.1 |  | 25.1 |  | 65
capacitor on holdup PCBA | [5 empty] | 26 | 42.7 | 50.8 | 57.1 |  |  |  | 25.1 |  | 25.1
Hold up PCB under power device | [5 empty] | 26.1 | 55.4 | 61.9 | 61.3 |  |  |  | 25.1 |  | 25.1
Derating - After temperature stablization has reached and test above completed, increase ambient temperature to 50 C and verify derating function (current limited to 125A) as well as new stablization results. | [17 empty] | Same question
TC Channel & Location | [5 empty] | 0 min | 15 | 30 | 45 | 60 | 75 | Ambient[C] | Correction[C] | Max Temp Recorded[C] | Corrected[C] | Max temperature [C] | Rise [C] | data logger file
Eaton branch breaker 125A plastic (top) | [12 empty] | 25.1 |  | 25.1 | 125
Eaton branch breaker 125A plastic (middle) | [12 empty] | 25.1 |  | 25.1 | 125
Eaton branch breaker 125A bussing (top) | [12 empty] | 25.1 |  | 25.1 |  | 65
Eaton branch breaker 125A bussing (middle) | [12 empty] | 25.1 |  | 25.1 |  | 65
To Comply:
The equipment shall not attain a temperature at any point sufficiently high to constitute a risk of fire, to damage any materials employed in the equipment, or to exceed the temperature rises specified in UL 916, Table 42.1
Intertek Comments:
The product complies with all applicable requirements of this test.
The product does not comply with the requirements of this test.
| Test Date: | [5 empty] | Tested By: |  | E Countrywood
Environmental Conditions During Testing: |  |  | Humidity: |  |  |  |  | Pressure: |  | NR |  |  | Ambient:
Equipment Used (See page 2 for details):
Note on T50: Dipesh Patel Intertek: please provide data sheet.
Note on A58: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Dipesh: See picture for L1 & L2 Neutral Balancer relay "busbars" Location OK?
Note on T60: Dipesh Patel Intertek: please provide datasheet
Note on T61: Dipesh Patel Intertek: please provide datasheet